As-built Specifications

Standards Manual

Last Modified: April 28, 2016

Clay County Utility Authority 3176 Old Jennings Road Middleburg, Florida 32068

(904) 272-5999

Contents

- Acronyms List	3

- Purpose	3

- Specifications	3

  - General	3

  - Configuration Standards	4

  - Cost	9

  - Submission of As-builts	10

  - Asset Table Worksheet	13

  - Layer Name Format	15

  - Block Naming	20

- Revision History	21

# Acronyms List

The following lists of acronyms are referenced throughout this standards manual.

| Acronym | Description |
| --- | --- |
| CAD | Computer Aided Drafting; refers to AutoCAD drawings |
| CCUA | Clay County Utility Authority |
| QA/QC | Quality Assurance / Quality Control |
| Engineer | Florida Licensed Professional Engineer |
| Surveyor | Florida Licensed Professional Surveyor |
| Contractor | Florida Licensed Underground Utility Contractor |

# Purpose

CCUA has released new specification standards for all submitted as-built drawings. The changes detailed below are effective immediately, so it’s important to review this document and consult CCUA with any questions. All referenced material will be provided as an electronic download (e.g., AutoCAD templates), which can be retrieved from CCUA’s website.

# Specifications

## General

    - Prior to completion of the final inspection, the Contractor shall provide to CCUA an electronic file and certified copies of as-built surveys with all required revisions included as the final as-built survey.

    - All changes requested by CCUA must be made to the electronic file, as well as the printed, signed and sealed copies. Neglecting to provide the required information will delay the final inspection.

    - All measurements are to be made by the Surveyor or Engineer who will be certifying the project as constructed.

    - The Contractor is responsible for coordinating with the Surveyor or Engineer during construction and shall provide access to all utilities prior to being buried; allowing accurate horizontal and vertical measurements to be acquired by the Surveyor or Engineer. In the event of any discrepancies identified by CCUA and at no cost to CCUA, the Contractor shall verify the location and measurements of any buried utilities.

    - Any and all utility information must be collected, regardless of “typical” alignments (including existing obstructing, conflicting, or crossing utility infrastructure). Refer to the information provided in the contract documents (construction plans, specifications, etc.).

    - The Surveyor or Engineer must provide CCUA with a certificate of its professional liability coverage that is no less than one million dollars ($1,000,000.00) and which names CCUA as an additional insured.

## Configuration Standards

    - All electronic as-built utility information in the as-built survey must reference the State Plane Coordinate System, Florida East Zone, NAD 83 2011 (horizontal) and NAVD 88 (vertical) utilizing GEOID12A or GEOID12B; the units must be in feet, and be properly projected into its correct spatial location prior to submitting to CCUA. CCUA will not re- project or manipulate as-built surveys in an attempt to correct improperly spatially referenced as-built surveys. It’s the certifying Surveyor or Engineer’s responsibility to ensure all submitted information adheres to the specifications.

      - The Surveyor performing the data collection will independently verify the positional accuracy relative to the referenced horizontal and vertical datum. Local, state or federal agencies vertical and horizontal control points will be used and are independent of checks to local project controls.

      - The positional accuracy relative to the referenced published control points used shall not exceed 0.5’ horizontally and 0.1’ vertically for water and reclaimed water utilities and 0.01’ vertically for sewer utilities.

      - Coordinates on the utility mains will be required at all pipe dead ends, size changes, points of connection to existing system, fittings (bends, valves, tees, plugs, etc.), at intersections of pipe, at 100’ intervals for water mains and 500’ intervals for reclaimed and force mains, or to the nearest fitting/structure whichever is less.

      - Intended Display Scale: All maps or reports of surveys produced and delivered with digital coordinate files must contain a statement to the effect of: “Map is intended to be displayed at a scale of 1”=60’.

    - File format shall be AutoCAD (.dwg), saved as version 2007 or higher.

    - All polylines (water, wastewater and reclaimed utility mains, etc.) shall be connected with no broken segments; unless noted in item a) below.

      - Polylines shall be broken at each of the following points (fittings / blocks in AutoCAD)

        - Valves (does NOT include Air Release Valves)

        - Reducers

        - Tees, Taps and Crosses (including Fire Hydrant Tees)

        - Caps (Tapped Caps)

        - Manholes

        - Clean-outs

        - R.P.Z. B.F.P. (Back-flow Preventer)

        - In-line Ball Valve

        - Point of service

        - Double Detector Check Valves & Check Valves

        - Adapters Couplings (including HDPE-to-PVC, HYMAX and Type of Material Transition Points, etc…)

### **DO NOT BREAK at any fittings not listed above. **

    - Gravity main lines shall be entered as a single line, digitized in the direction of the design flow and broken at manholes. The beginning point of the line would be the upstream end and the ending point would be the downstream end.

    - Force main lines shall be entered as a single line, digitized in the direction of the design flow and broken at items identified in item 3.a) above. The beginning point of the line would be the upstream end and the ending point would be the downstream end.

    - All water, sewer and reclaimed water utility mains shall show a call out designating each size, material, pipe rating and class of pipe installed and include a leader line pointing to the pipe.

      - Additionally, gravity sewer mains shall be identified with the length and slope information, matching the sewer schedule (see item D.4 below).

      - Changes in material for water, sewer and reclaimed mains shall be identified with a call out (e.g., Ductile Iron to PVC).

    - All new and existing utilities (water, sewer, reclaimed, electrical, communications, etc…) and drainage located within lift station, treatment plant and well sites impacted by construction shall be located relative to property lines and/or right-of-way lines, using the specifications identified in this document.

    - The Surveyor or Engineer shall provide a Boundary Survey as defined in 5J-17.052(2) of the Standards of Practice of the site showing above and below ground improvements impacted by construction within lift station, treatment plant and well sites. All infrastructure, equipment and lines that are necessary for full operation of the site shall be included. Elevations shall be indicated at the finished floor and top of structures and at pipe inverts, wet well tops (rim elevation), wet well sumps and at ground level adjacent to wet wells.

    - Directional drill logs shall be provided and show profile details on the corresponding drawing(s).

    - Blocks inserted into a drawing shall be on the correct layer, identifying those features (including service type).

    - Pre-configured block tool palettes have been provided.

      - Make sure to rename the block(s) using the XX or RENAME command, if the desired block is not available within the tool palette.

    - All text (DTEXT and MTEXT) must be masked; CUT/BROKEN LINES BEHIND TEXT WILL NOT BE ACCEPTED. Detail(s) also must be masked using the wipeout command. The dimensions will be created with masked text using a standard dimension style(s) located within the CCUA template.

    - All dimensioning, text and multileader lines must be drawn using CCUA’s provided template (each template has been preconfigured).

      - Set the ‘Dimension Association’ to 2 (exploded dimensions will not be accepted).

      - The templates are set to use Arial font, and have been named as follows: CCUA Annotative Text, CCUA Standard Dimension and CCUA Annotative Leader.

    - All corresponding linetypes must be used.

    - Text identifying information about features shall be properly aligned. Text shall be visible on the drawing using the template font style provided and with the base set to the upper left-hand corner of the text which is clear of the linear or block features. For legibility, it may require that the label be moved and accompanied by a leader arrow. The labels shall be placed onto a separate layer and not to be placed on the feature layer itself. Labels must be properly rotated for easy legibility (horizontal alignment).

    - Features shall be placed on their appropriate layers and assigned colors by layer for consistency (see F below). Features shown in the AutoCAD files shall be in model space and be contained in the AutoCAD files as opposed to being linked through externally referenced files (binded layers MUST reflect the correct layers).

      - Separate AutoCAD layout tabs are required for water, sewer, reclaimed water, and lift station as-builts.

    - The AutoCAD file shall be reviewed for duplicate objects.

    - Polylines shall be continuous from structure to structure (see item 3.a) above). End points of polylines must be snapped to the end points of connecting polylines, with a structure node being snapped to the end point.

    - The following list of section should be referenced when creating AutoCAD as-built surveys.

      - Clean all unnecessary layers and blocks before submitting final as- built plans to CCUA

      - Use only CCUA approved layers (see F below)

      - Properly place features on the correct AutoCAD layers

      - Do not break lines or trim behind text boxes; utilize the text masking feature (also applies to detail blow ups)

      - Use reasonably scaled templates and blocks for all drawings

      - Add continuations / match lines on all related as-builts

      - Do not explode blocks, even if object is owned by others

      - Snap all designated blocks at the base point of the object

      - Properly connect all lines, blocks, etc.

      - Create detail blow-ups to show information in close proximity (to maintain legibility)

    - Layer naming conventions shall follow the NCS (National CAD Standards) guidelines. CCUA’s base layers (see F below) will be provided inside of the template AutoCAD file, any other layer(s) added must follow the NCS documentation. For more information on NCS, visit their website at http://www.nationalcadstandard.org/.

    - Each  block (e.g., hydrant, valves, mains, etc.) shall have feature IDs assigned by the Surveyor or Engineer completing the as-builts, which reference a worksheet table. The worksheet table will contain an inventory of items installed. The entire table must be complete and refer to a corresponding feature on the as-builts (see item E.1 below)

      - Pre-configured block tool palettes are available on CCUA’s website, located on the development and permitting section.

      - As blocks are added from the provided tool palettes, a dialog window will prompt asking for the feature ID. For consistency add the sequential number at the end of the feature ID (e.g., WM_VALVE_1, WM_VALVE_2, WM_VALVE_3, etc… see G below for more examples).

    - All AutoCAD drawing text annotation, detail blow-ups, and dimensions shall be shown in Model Space. The Contractor, Surveyor or Engineer’s title block shall be shown in the layout Viewport.

## Cost

    - The as-built surveys shall be prepared at the Contractor's, or Developer’s (applicant) expense.

    - The applicant’s Contractor shall be responsible for paying in advance to CCUA, the cost for reviewing the final as-built surveys for each extension of the CCUA’s utility system. The cost is based on the CCUA’s initial estimate of the time needed to review the final as-built surveys.

    - Extra time required to review the as-built surveys, due to failure of meeting the as-built specifications or for other inadequate or inaccurate information required of applicant’s Surveyor or Contractor to complete CCUA’s as-built drawings or by any combination of such factors shall be charged to and paid by the applicant as an additional cost of completing CCUA’s final CAD as-built plans, based on a rate of $35.00 per hour, plus plotting cost for any extra proof sets.

## Submission of As-builts

    - As-built surveys shall be submitted using CCUA’s AutoCAD template settings; with the Contractor, Surveyor or Engineer’s title block. Sheets shall be 22”x34” and accompanied by all necessary electronic files delivered on CD/DVD or by e-mail.

      - Scale shall range between 1”=10’ to 1” = 60’, unless approved by CCUA.

      - Each sheet must be labeled “AS-BUILT” in one-inch high bold letters in the bottom right hand corner and include the following items:

        - Station numbers and with offsets

        - Dimension measurements

        - Lot numbers

        - Street names

        - Scale

        - Location, elevation and datum of the benchmark used

        - Easements as shown on approved plans

        - Certification block (see 3 below)

        - Any other additional requirements as outlined by the Standards of Practice per the Florida Administrative code for Surveying and Mapping

    - Once CCUA has completed its proposed final review of the CAD as-built plans for such extension, a proof set of the proposed plans will be provided to the Contractor for proofreading and verification of the accuracy of CCUA’s proposed final CAD as-built drawings, based on the information provided to CCUA by the applicant, Contractor or Surveyor. When CCUA’s proposed final CAD as-built drawing have been verified as accurate by the Contractor and CCUA, then a final set of "official" as-built drawing will be plotted by the CCUA and will be prepared and submitted for the signature of the Surveyor and/or Engineer.

    - Each as-built survey sheet is required to have a certification block (as shown below) and bear the name, address, phone number and signature of the Contractor, and Surveyor or Engineer. The Surveyor will certify the horizontal and vertical dimensions and elevations of the project’s as-built conditions. The Engineer shall certify the project has been constructed in substantial conformance with the permitted construction plans and specifications. The Contractor will certify that materials and quantities used were accurate and are in accordance with CCUA’s approved plans and specifications. The signature(s) certify the as-built survey and information provided is accurate.

      - As-built certification block for the Surveyor:

      - As-built certification block for the Engineer:

      - As-built certification block for the Contractor:

    - A signed sealed written report in a format acceptable to CCUA (see item

      - below) by the Surveyor or Engineer which identifies each manhole by reference number, identifies the inverts of all pipes entering and leaving the manhole, and provides the distance and grade of each pipe between manholes.

a)	In addition to any written report(s); report information shall be provided in an electronic Microsoft Excel file, which properly identifies columns (e.g., Reference ID, N. Invert, S. Invert, etc.). A template file can be found on CCUA’s website.

## Asset Table Worksheet

    - The following list of information shall be collected and turned in as an electronic Microsoft Excel file on CD/DVD, or sent by e-mail. A template file has already been created and is available on CCUA’s website for download.

| Fire Hydrants | Valves | RPZ |
| --- | --- | --- |
| Feature ID | Feature ID | Feature ID |
| Plan Sheet Number | Plan Sheet Number | Plan Sheet Number |
| Easting (X) | Easting (X) | Easting (X) |
| Northing (Y) | Northing (Y) | Northing (Y) |
| Model Number | Valve Type | Size of RPZ |
| Manufacturer | Direction to Open | Year of Installation |
| Direction to Open | Valve Size | Type of Joint Fitting |
| Fire Hydrant Size | Year of Installation | Material Transition |
| Year of Installation | Type of Joint Fitting | Owned By |
| Date of Installation | Main Type |  |
| Main Size @ F.H. Connection | Model Number |  |
| Manufacturer Year | Manufacturer |  |
| Owned By | Turns to Open |  |
| Material Transition |  |  |
| Survey Elevation |  |  |
| Owned By |  |  |

| Fittings | Locate Wire | Lift Station |
| --- | --- | --- |
| Feature ID | Feature ID | Feature ID |
| Plan Sheet Number | Plan Sheet Number | Plan Sheet Number |
| Easting (X) | Easting (X) | Easting (X) |
| Northing (Y) | Northing (Y) | Northing (Y) |
| Main Type | Main Type | Inv. Elevation In |
| Fitting Type | Owned By | Inv. Elevation In |
| Fitting Size |  | Inv. Elevation In |
| Material Type |  | Inv. Elevation Out |
| Year of Installation |  | Top Elevation |
| Type of Joint Fitting |  | Bottom Elevation |
| Owned By |  | Lift Station Diameter |
| Survey Elevation |  | Owned By |
| Material Transition |  |  |

| Manhole | Cleanout | Bends |
| --- | --- | --- |
| Feature ID | Feature ID | Feature ID |
| Plan Sheet Number | Plan Sheet Number | Plan Sheet Number |
| Design Manhole Number | Easting (X) | Main Type |
| Easting (X) | Northing (Y) | Fitting Size |
| Northing (Y) | Cleanout Size | Material Type |
| Rim Elevation | Inv. Elevation | Year of Installation |
| Invert Elevation North | Top Elevation | Type of Joint Fitting |
| Invert El. Northeast | Year of Installation | Used to Avoid Conflict |
| Invert El. East |  | Degree (of bend) |
| Invert El. Southeast |  | Survey Elevation |
| Invert El. South |  | Material Transition |
| Invert El. Southwest |  |  |
| Invert El. West |  |  |
| Invert El. Northwest |  |  |
| Year of Installation |  |  |

### Casing

Feature ID

Plan Sheet Number Casing Size

Year of Installation Main Type Material Type Upstream Invert Downstream Invert Owned By

Survey Elevation

## Layer Name Format

    - Discipline Designator Values:

Discipline identifier (value), which is added to the layer name (e.g., CU- WATR-DOMC-PIPE-XXXX XXXX XXXX XXXX XX-ST) the value

must be four characters in length (see table below).

| Designator | Description |
| --- | --- |
| C | Civil |
| CU | Civil Utilities |
| V | Survey / Mapping |
| VU | Survey / Mapping Utilities |

    - Layer:

AutoCAD drawing layer name, which follow the National CAD Standards

(e.g., CU-WATR-DOMC-PIPE-XXXX XXXX XXXX XXXX XX-ST)

the value must be four characters in length (see table below).

| Name | Color | Linetype | Description |
| --- | --- | --- | --- |
| C-ANNO-MATL | White | PHANTOM2 | Match line annotation |
| C-ANNO-NOTE | Yellow | Continuous | Note annotation |
| C-ANNO-TTLB | White | Continuous | Title block annotation |
| C-BLDG-ANNO | White | Continuous | Building annotation |
| C-BLDG-STRC | 15 | Continuous | Building structure |
| C-ESMT-ANNO | White | Continuous | Easement annotation |

| C-ESMT-LINE | White | HIDDEN | Easement line |
| --- | --- | --- | --- |
| C-POND-ANNO | 15 | Continuous | Pond annotation |
| C-POND-LINE | 15 | HIDDEN | Pond line |
| C-PROP-ANNO | White | Continuous | Property annotation |
| C-PROP-LINE | 53 | DASHDOT2 | Property line |
| C-ROAD-CNTR | 10 | CENTER2 | Roadway center line |
| C-ROAD-CURB | 251 | Continuous | Roadway curb / edge |
| C-ROAD-RWAY | White | PHANTOM2 | Roadway right-of-way |
| C-ROAD-SWLK | 251 | Continuous | Roadway sidewalk |
| C-STRM-ANNO | 15 | Continuous | Storm annotation |
| C-STRM-LINE | 15 | Continuous | Storm line |
| CU-ELEC-ANNO | Yellow | Continuous | Electrical annotation |
| CU-ELEC-JUNC | 14 | Continuous | Electrical junction |
| CU-ELEC-LINE | 14 | HIDDEN | Electrical line |
| CU-SSWR-FORC-ANNO | 41 | Continuous | Sewer forced annotation |
| CU-SSWR-FORC-DETL | 41 | Continuous | Sewer forced detail |
| CU-SSWR-FORC-INFS | 30 | Continuous | Sewer forced infrastructure |
| CU-SSWR-FORC-PIPE-XXXX XXXX XXXX XXXX XX-ST | 30 | Continuous | Sewer forced pipe |
| CU-SSWR-FORC-SRVC | 34 | Continuous | Sewer forced service |
| CU-SSWR-GRAV-ANNO | 81 | Continuous | Sewer gravity annotation |
| CU-SSWR-GRAV-DETL | 81 | Continuous | Sewer gravity detail |
| CU-SSWR-GRAV-INFS | GREEN | Continuous | Sewer gravity infrastructure |
| CU-SSWR-GRAV-PIPE-XXXX XXXX XXXX XXXX XX-ST | GREEN | Continuous | Sewer gravity pipe |
| CU-SSWR-GRAV-SRVC | 106 | Continuous | Sewer gravity service |
| CU-SSWR-STRC-LIFT | Yellow | Continuous | Sewer Lift Station structure |
| CU-WATR-DOMC-ANNO | 143 | Continuous | Water domestic annotation |
| CU-WATR-DOMC-DETL | 143 | Continuous | Water domestic detail |
| CU-WATR-DOMC-INFS | Cyan | Continuous | Water domestic infrastructure |
| CU-WATR-DOMC-PIPE-XXXX XXXX XXXX XXXX XX-ST | Cyan | Continuous | Water domestic pipe |
| CU-WATR-DOMC-SRVC | 154 | Continuous | Water domestic service |
| CU-WATR-RECL-ANNO | 191 | Continuous | Water reclaimed annotation |
| CU-WATR-RECL-DETL | 191 | Continuous | Water reclaimed detail |
| CU-WATR-RECL-INFS | 190 | Continuous | Water reclaimed infrastructure |
| CU-WATR-RECL-PIPE-XXXX XXXX XXXX XXXX XX-ST | 190 | Continuous | Water reclaimed pipe |
| CU-WATR-RECL-SRVC | 185 | Continuous | Water reclaimed service |

*Layers not included in list shall be added following the NCS guidelines. CCUA shall be provided a list

of any new layers added.

    - Size Values:

Size identifier (value), which is added to the layer name (e.g., CU-WATR- DOMC-PIPE-XXXX XXXX XXXX XXXX XX-ST) the value must be four characters in length (see table below).

| Size* | Description |
| --- | --- |
| 0.25 | 1/4" |
| 0.50 | 1/2" |
| 0.75 | 3/4" |
| 1.25 | 1-1/4" |
| 1.50 | 1-1/2" |
| 1.75 | 1-3/4" |
| 2.00 | 2" |
| 2.25 | 2-1/4" |
| 2.50 | 2-1/2" |
| 3.00 | 3" |
| 4.00 | 4" |
| 6.00 | 6" |
| 8.00 | 8" |
| 10.0 | 10" |
| 12.0 | 12" |
| 14.0 | 14" |
| 16.0 | 16" |
| 18.0 | 18" |
| 20.0 | 20" |
| 24.0 | 24" |
| 30.0 | 30" |
| 36.0 | 36" |

*Values not included in list shall be added and abbreviated with four (4)

characters. CCUA shall be provided a list of any new values added.

    - Material Values:

Material identifier (value), which is added to the layer name (e.g., CU- WATR-DOMC-PIPE-XXXX XXXX XXXX XXXX XX-ST) the value

must be four characters in length (see table below).

| Identifier* | Description |
| --- | --- |
| CIRN | Cast Iron |
| DIRN | Ductile Iron |
| FPVC | Fusible Polyvinyl Chloride |

| HDPE | High-Density Polyethylene |
| --- | --- |
| PVC~ | Polyvinyl Chloride |
| SSTL | Stainless Steel |
| STEL | Steel |

*Values not included in list shall be added and abbreviated with four (4)

characters. CCUA shall be provided a list of any new values added.

    - Class Values:

Class identifier (value), which is added to the layer name (e.g., CU- WATR-DOMC-PIPE-XXXX XXXX XXXX XXXX XX-ST) the value

must be four characters in length (see table below).

| Designator* | Description |
| --- | --- |
| 0000 | Not Applicable |
| 0051 | Class 51 |
| 0150 | Class 150 |
| 0300 | Class 300 |
| 0900 | Class 900 |
| 0905 | Class 905 |

*Values not included in list shall be added and abbreviated with four (4)

characters. CCUA shall be provided a list of any new values added.

    - Rating Values:

Rating identifier (value), which is added to the layer name (e.g., CU- WATR-DOMC-PIPE-XXXX XXXX XXXX XXXX XX-ST) the value

must be four characters in length (see table below).

| Identifier* | Description |
| --- | --- |
| 0000 | Not Applicable |
| DR09 | Dimension Ratio (DR) is 9 |
| DR11 | Dimension Ratio (DR) is 11 |
| DR18 | Dimension Ratio (DR) is 18 |
| DR21 | Dimension Ratio (DR) is 21 |
| DR25 | Dimension Ratio (DR) is 25 |
| DR26 | Dimension Ratio (DR) is 26 |
| DR35 | Dimension Ratio (DR) is 35 |
| SC40 | Schedule 40 |
| SC80 | Schedule 80 |

*Values not included in list shall be added and abbreviated with four (4)

characters. CCUA shall be provided a list of any new values added.

    - Construction Values:

Construction identifier (value), which is added to the layer name (e.g., CU-WATR-DOMC-PIPE-XXXX XXXX XXXX XXXX XX-ST) the

value must be four characters in length (see table below).

| Identifier* | Description |
| --- | --- |
| DD | Directional Drill |
| JB | Jack and Bore |
| OC | Open-cut |
| PB | Pipe Burst |
| PP | Pipe Push |

*Values not included in list shall be added and abbreviated with two (2)

characters. CCUA shall be provided a list of any new values added.

    - Status Field Codes:

Status identifier (code), which is added to the end of the layer name (e.g., CU-WATR-DOMC-PIPE-XXXX XXXX XXXX XXXX XX-ST)

| Code | Description |
| --- | --- |
| A | Abandoned |
| D | Existing to demolish |
| E | Existing to remain |
| F | Future work |
| M | Items to be moved |
| N | New work |
| O | Owned by others |

    - Examples:

Layer Name

CU-SSWR-GRAV-PIPE-4.00 PVC~ 0000 DR26 OC CU-SSWR-FORC-PIPE-4.00 PVC~ 0900 DR18 OC CU-SSWR-FORC-PIPE-8.00 DIRN 0051 DR18 OC CU-WATR-DOMC-PIPE-2.00 PVC~ 0000 SC80 OC CU-WATR-DOMC-PIPE-36.0 PVC~ 0900 DR21 OC CU-WATR-RECL-PIPE-4.00 PVC~ 0900 DR21 OC

## Block Naming

| Block Name | Feature ID | Layer | Description |
| --- | --- | --- | --- |
| WM_TEE WM_RPZ | WM_TEE_* WM_RPZ_* | CU-WATR-DOMC-INFS CU-WATR-DOMC-INFS | Water Tee/Tap Water Reduced Pressure valve PressPressure Zone |
| WM_CV | WM_CV_* | CU-WATR-DOMC-INFS | Water Check Valve |
| WM_DBLCV | WM_DBLCV_* | CU-WATR-DOMC-INFS | Water Double Detector Check Valve |
| WM_DIA_APT_COUPLING | WM_DIA_APT_COUPLING_* | CU-WATR-DOMC-INFS | Water Coupling |
| WM_SLEEVE | WM_SLEEVE_* | CU-WATR-DOMC-INFS | Water Sleeve |
| WM_FLUSHHYD | WM_FLUSHHYD_* | CU-WATR-DOMC-INFS | Water Flushing Hydrant |
| WM_LWBOX | WM_LWBOX_* | CU-WATR-DOMC-INFS | Water Locate Wire Box |
| WM_METER | WM_METER_* | CU-WATR-DOMC-INFS | Water Meter |
| WM_TAP_CAP_wFLHYD | WM_TAP_CAP_wFLHYD_* | CU-WATR-DOMC-INFS | Water Tap Cap |
| WM_FIREHYD | WM_FIREHYD_* | CU-WATR-DOMC-INFS | Water Fire Hydrant |
| WM_PLUG | WM_PLUG_* | CU-WATR-DOMC-INFS | Water Plug/Cap |
| WM_VALVE | WM_VALVE_* | CU-WATR-DOMC-INFS | Water Valve |
| WM_ARV | WM_ARV_* | CU-WATR-DOMC-INFS | Water Air Release Valve |
| WM_REDUCER | WM_REDUCER_* | CU-WATR-DOMC-INFS | Water Reducer |
| WM_CROSS | WM_CROSS_* | CU-WATR-DOMC-INFS | Water Cross |
| WM_11.25BEND | WM_11.25BEND_* | CU-WATR-DOMC-INFS | Water 11.25˚ Bend |
| WM_22.5BEND | WM_22.5BEND_* | CU-WATR-DOMC-INFS | Water 22.5˚ Bend |
| WM_45BEND | WM_45BEND_* | CU-WATR-DOMC-INFS | Water 45˚ Bend |
| WM_90BEND | WM_90BEND_* | CU-WATR-DOMC-INFS | Water 90˚ Bend |
| WM_BEND_TURNED | WM_BEND_TURNED_* | CU-WATR-DOMC-INFS | Water Bend Turned |
| WM_CASING | WM_CASING_* | CU-WATR-DOMC-INFS | Water Main Casing |
| RE_TEE RE_CV | RE_TEE_* RE_CV_* | CU-WATR-RECL-INFS CU-WATR-RECL-INFS | Reuse Tee/Tap Reuse Check Valve |
| RE_DBLCV | RE_DBLCV_* | CU-WATR-RECL-INFS | Reuse Double Detector Check Valve |
| RE_DIA_APT_COUPLING | RE_DIA_APT_COUPLING_* | CU-WATR-RECL-INFS | Reuse Coupling |
| RE_SLEEVE | RE_SLEEVE_* | CU-WATR-RECL-INFS | Reuse Sleeve |
| RE_FLUSHHYD | RE_FLUSHHYD_* | CU-WATR-RECL-INFS | Reuse Flushing Hydrant |
| RE_LWBOX | RE_LWBOX_* | CU-WATR-RECL-INFS | Reuse Locate Wire Box |
| RE_METER | RE_METER_* | CU-WATR-RECL-INFS | Reuse Meter |
| RE_TAP_CAP_wFLHYD | RE_TAP_CAP_wFLHYD_* | CU-WATR-RECL-INFS | Reuse Tap Cap |
| RE_FIREHYD | RE_FIREHYD_* | CU-WATR-RECL-INFS | Reuse Fire Hydrant |
| RE_PLUG | RE_PLUG_* | CU-WATR-RECL-INFS | Reuse Plug/Cap |
| RE_VALVE | RE_VALVE_* | CU-WATR-RECL-INFS | Reuse Valve |
| RE_ARV | RE_ARV_* | CU-WATR-RECL-INFS | Reuse Air Release Valve |
| RE_REDUCER | RE_REDUCER_* | CU-WATR-RECL-INFS | Reuse Reducer |
| RE_CROSS | RE_CROSS_* | CU-WATR-RECL-INFS | Reuse Cross |
| RE_11.25BEND | RE_11.25BEND_* | CU-WATR-RECL-INFS | Reuse 11.25˚ Bend |
| RE_22.5BEND | RE_22.5BEND_* | CU-WATR-RECL-INFS | Reuse 22.5˚ Bend |

| RE_45BEND | RE_45BEND_* | CU-WATR-RECL-INFS | Reuse 45˚ Bend |
| --- | --- | --- | --- |
| RE_90BEND | RE_90BEND_* | CU-WATR-RECL-INFS | Reuse 90˚ Bend |
| RE_BEND_TURNED | RE_BEND_TURNED_* | CU-WATR-RECL-INFS | Reuse Bend Turned |
| RE_CASING | RE_CASING_* | CU-WATR-RECL-INFS | Reuse Main Casing |
| FM_CV | FM_CV_* | CU-SSWR-FORC-INFS | Force Main Check Valve |
| FM_DBLCV | FM_DBLCV_* | CU-SSWR-FORC-INFS | Force Main Double Detector Check Valve |
| FM_DIA_APT_COUPLING | FM_DIA_APT_COUPLING_* | CU-SSWR-FORC-INFS | Force Main Coupling |
| FM_SLEEVE | FM_SLEEVE_* | CU-SSWR-FORC-INFS | Force Main Sleeve |
| FM_FLUSHHYD | FM_FLUSHHYD_* | CU-SSWR-FORC-INFS | Force Main Flushing Hydrant |
| FM_LWBOX | FM_LWBOX_* | CU-SSWR-FORC-INFS | Force Main Locate Wire Box |
| FM_TAP_CAP_wFLHYD | FM_TAP_CAP_wFLHYD_* | CU-SSWR-FORC-INFS | Force Main Tap Cap |
| FM_PLUG | FM_PLUG_* | CU-SSWR-FORC-INFS | Force Main Plug/Cap |
| FM_VALVE FM_TEE | FM_VALVE_* FM_TEE_* | CU-SSWR-FORC-INFS CU-SSWR-FORC-INFS | Force Main Valve Force Main Tee/Tap |
| FM_ARV | FM_ARV_* | CU-SSWR-FORC-INFS | Force Main Air Release Valve |
| FM_FMDUCER | FM_FMDUCER_* | CU-SSWR-FORC-INFS | Force Main Reducer |
| FM_CROSS | FM_CROSS_* | CU-SSWR-FORC-INFS | Force Main Cross |
| FM_11.25BEND | FM_11.25BEND_* | CU-SSWR-FORC-INFS | Force Main 11.25˚ Bend |
| FM_22.5BEND | FM_22.5BEND_* | CU-SSWR-FORC-INFS | Force Main 22.5˚ Bend |
| FM_45BEND | FM_45BEND_* | CU-SSWR-FORC-INFS | Force Main 45˚ Bend |
| FM_90BEND | FM_90BEND_* | CU-SSWR-FORC-INFS | Force Main 90˚ Bend |
| FM_BEND_TURNED | FM_BEND_TURNED_* | CU-SSWR-FORC-INFS | Force Main Bend Turned |
| FM_CASING | FM_CASING_* | CU-SSWR-FORC-INFS | Force Main Casing |
| SS_PLUG | SS_PLUG_* | CU-SSWR-GRAV-INFS | Gravity Sewer Plug |
| SS_MANHOLE | SS_MANHOLE_* | CU-SSWR-GRAV-INFS | Gravity Sewer Plug |
| SS_CLEANOUT | SS_CLEANOUT_* | CU-SSWR-GRAV-INFS | Gravity Sewer Plug |

# Revision History

| Revision | Date | Employee | Description |
| --- | --- | --- | --- |
| 1 | 12/09/2013 | Daniel Johns | Clarification of III.B.8 |
| 2 | 02/26/2014 | Daniel Johns | Q1 of 2014: Revisions to III.B.1.a); III.B.16; III.B.19.b); III.B.20; III.D.3 and addition of III.F |
| 3 | 10/30/2014 | Daniel Johns | Q4 of 2014: Revisions to B.1, B.21, D.1, E.1 and added section G |
| 4 | 04/27/2016 | Daniel Johns | Q2 of 2016: Revisions to B.1, B.21, D.1, D.3.a, E and added B.22, D.1.b.9, and G |
| 5 |  |  |  |
| 6 |  |  |  |
| 7 |  |  |  |